{"text_format":"1","workbook":"xlsx","n_sheets":1,"sheets":["TEWI"],"not_rendered":{"charts":0,"images":1,"macros":0,"external_links":0,"defined_names":3,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"TEWI","index":0,"n_rows":41,"n_cols":11,"rows_kept":41,"cut":false,"hidden":false,"merged":[[6,3,7,6],[1,1,1,6],[2,3,2,6]]}
[null,null,null,null,null,null,null,null,null,"Jazyk:",1]
[null,{"$f":"CHOOSE(jazyk,\"TEWI - Standardní metoda kalkulace\",\"TEWI - Standard Method of Calculation\")","v":"TEWI - Standardní metoda kalkulace"}]
[null,{"$f":"CHOOSE(jazyk,\"Název akce:\",\"Job Reference:\")","v":"Název akce:"},null,"Remodelling technologie chlazení MAKRO České Budějovice"]
[null,{"$f":"CHOOSE(jazyk,\"Datum:\",\"Date:\")","v":"Datum:"}]
[]
[null,{"$f":"CHOOSE(jazyk,\"VSTUPNÍ DATA\",\"INPUT DATA\")","v":"VSTUPNÍ DATA"}]
[null,null,{"$f":"CHOOSE(jazyk,\"Obor aplikace:\",\"Application Sector:\")","v":"Obor aplikace:"},null,null,null,null,null,1]
[]
[]
[null,null,{"$f":"CHOOSE(jazyk,\"Druh chladiva:\",\"Refrigerant Fluid:\")","v":"Druh chladiva:"},{"$f":"REPT(\".\",100)","v":"...................................................................................................."},null,"-",null,null,2]
[null,null,{"$f":"CHOOSE(jazyk,\"Náplň chladiva:\",\"Refrigerant Charge:\")","v":"Náplň chladiva:"},{"$f":"REPT(\".\",100)","v":"...................................................................................................."},null,"kg",null,null,3]
[]
[null,null,{"$f":"CHOOSE(jazyk,\"Roční spotřeba energie:\",\"Annual Energy Consumption:\")","v":"Roční spotřeba energie:"}]
[null,null,{"$f":"CHOOSE(jazyk,\"Kompresory:\",\"Compressors:\")","v":"Kompresory:"},{"$f":"REPT(\".\",100)","v":"...................................................................................................."},null,"kWh",null,null,4]
[null,null,{"$f":"CHOOSE(jazyk,\"Příslušenství:\",\"Ancillary:\")","v":"Příslušenství:"},"....................................................................................................",null,"kWh",null,null,5]
[]
[null,{"$f":"CHOOSE(jazyk,\"OBOROVÉ UKAZATELE:\",\"SECTORAL FACTORS:\")","v":"OBOROVÉ UKAZATELE:"},null,null,null,null,null,null,null,"Kategorie:",1]
[null,null,{"$f":"CHOOSE(jazyk,\"Životnost zařízení:\",\"System Operational Lifetime:\")","v":"Životnost zařízení:"},null,{"$f":"REPT(\".\",100)","v":"...................................................................................................."},{"$f":"CHOOSE(jazyk,\"roky\",\"yr\")","v":"roky"},{"$f":"CHOOSE(kategorie,10,10,10,10)","v":10},null,6]
[null,null,{"$f":"CHOOSE(jazyk,\"GWP chladiva:\",\"Refrigerant GWP:\")","v":"GWP chladiva:"},{"$f":"REPT(\".\",100)","v":"...................................................................................................."},null," ",null,null,7]
[]
[null,null,"L1:",{"$f":"REPT(\".\",100)","v":"...................................................................................................."},null,"%",{"$f":"CHOOSE(kategorie,5,2,0,0)","v":5},null,8]
[null,null,"L2:","....................................................................................................",null,"%",{"$f":"CHOOSE(kategorie,0,0.5,0,0)","v":0},null,9]
[null,null,"S1:","....................................................................................................",null,"%",{"$f":"CHOOSE(kategorie,0.25,0.25,0,0)","v":0.25},null,10]
[null,null,"S2:","....................................................................................................",null,"%",{"$f":"CHOOSE(kategorie,0,0,0,0)","v":0},null,11]
[null,null,{"$f":"CHOOSE(jazyk,\"Účinnost rekuperace:\",\"Recovery Efficiency:\")","v":"Účinnost rekuperace:"},"....................................................................................................",null," ",{"$f":"CHOOSE(kategorie,0.95,0.95,0.6,0.3)","v":0.95},null,12]
[null,null,{"$f":"CHOOSE(jazyk,\"Emisní faktor CO2, β (kg CO2/kWk):\",\"CO2 Emission Factor, β (kg CO2/kWk):\")","v":"Emisní faktor CO2, β (kg CO2/kWk):"},null,{"$f":"REPT(\".\",100)","v":"...................................................................................................."}," ",0.84,null,13]
[]
[null,{"$f":"CHOOSE(jazyk,\"KALKULACE TEWI:\",\"TEWI CALCULATION:\")","v":"KALKULACE TEWI:"}]
[null,{"$f":"CHOOSE(jazyk,\"a) Přímý efekt\",\"a) Direct Effect\")","v":"a) Přímý efekt"}]
[null,null,{"$f":"CHOOSE(jazyk,\"Ztráta chladiva (provozní):\",\"Refrigerant Release (Operational):\")","v":"Ztráta chladiva (provozní):"},null,{"$f":"REPT(\".\",100)","v":"...................................................................................................."},"kg",{"$f":"G11*G18*(G21+G22+G23+G24)/100","v":0},null,14]
[null,null,{"$f":"CHOOSE(jazyk,\"Ztráta chladiva (při likvidaci zařízení):\",\"Refrigerant Release (End of Life):\")","v":"Ztráta chladiva (při likvidaci zařízení):"},null,"....................................................................................................","kg",{"$f":"G11*(1-G25)","v":0},null,15]
[]
[null,null,{"$f":"CHOOSE(jazyk,\"Celková ztráta chladiva po dobu životnosti:\",\"Total Lifetime Refrigerant Release:\")","v":"Celková ztráta chladiva po dobu životnosti:"},null,{"$f":"REPT(\".\",100)","v":"...................................................................................................."},"kg",{"$f":"G30+G31","v":0},null,16]
[]
[null,null,{"$f":"CHOOSE(jazyk,\"Ekvivalent CO2:\",\"CO2 Equivalent:\")","v":"Ekvivalent CO2:"},{"$f":"REPT(\".\",100)","v":"...................................................................................................."},null,"kg",{"$f":"G33*G19","v":0},null,17]
[null,{"$f":"CHOOSE(jazyk,\"b) Nepřímý efekt\",\"b) Indirect Effect\")","v":"b) Nepřímý efekt"}]
[null,null,{"$f":"CHOOSE(jazyk,\"Nepřímý efekt:\",\"Indirect Effect:\")","v":"Nepřímý efekt:"},{"$f":"REPT(\".\",100)","v":"...................................................................................................."},null,"kg CO2",{"$f":"(G14+G15)*G26*G18","v":0},null,18]
[null,"c) TEWI"]
[null,null,"TEWI:",{"$f":"REPT(\".\",100)","v":"...................................................................................................."},null,"kg CO2",{"$f":"G35+G37","v":0},null,19]
[]
[null,"Vyplňte zelená pole v souladu s EN 378-2"]